# HX-200 Rooftop HVAC Unit – Service Manual

Model HX-200 · Revision 4 · Northwind Field Service · Fictional training document

# 1. Overview

The HX-200 is a 20 kW packaged rooftop heating, ventilation and air-conditioning unit used in hospitals, malls and offices. It has two refrigerant circuits, a condenser fan assembly and a microcontroller that shows fault codes on the service display.

# 2. Fault codes

| Code | Meaning | Likely cause | First action |
| --- | --- | --- | --- |
| E01 | High refrigerant pressure | Blocked condenser coil, failed condenser fan motor (HX-FAN-07), faulty high-pressure switch (HX-PS-HP) | Check condenser fan runs; clean coil; test pressure switch |
| E02 | Low refrigerant pressure | Refrigerant leak | Do NOT recharge without leak test. Refrigerant work needs an F-gas certified technician |
| E04 | Compressor fails to start | Failed run capacitor (HX-CAP-35), contactor fault | Isolate power, test capacitor; replace if outside 35 µF ±6% |
| E07 | Supply air sensor fault | Loose sensor plug, failed sensor | Re-seat plug; if code returns, replace sensor |
| E09 | Condenser fan overload | Seized bearing in HX-FAN-07, wiring fault | Isolate power; spin fan by hand; replace HX-FAN-07 if stiff or noisy |

# 3. Symptoms without a code

Unit runs but air is not cool, with no fault code: check filters (replace every 3 months), then check refrigerant pressures.

Loud grinding or squealing from the roof: almost always the condenser fan motor bearing (HX-FAN-07). Treat as E09.

Water dripping inside the building: blocked condensate drain. Clear the drain line; not a refrigerant leak.

# 4. Standard repair times

| Job | Time |
| --- | --- |
| Replace run capacitor | 45 min |
| Replace condenser fan motor | 2.5 hours |
| Replace high-pressure switch | 1.5 hours (includes refrigerant recovery) |
| Coil clean | 1 hour |

# 5. Safety

Always isolate and lock out electrical power before opening any panel.

Roof work requires a second person on site and fall protection.

Refrigerant handling requires an F-gas certified technician.