# PG-50 Standby Diesel Generator – Service Manual

Model PG-50 · Revision 2 · Northwind Field Service · Fictional training document

# 1. Overview

The PG-50 is a 50 kVA standby diesel generator that starts automatically when mains power fails. It is common at hospitals and data centres, where a failed start is critical.

# 2. Fault codes

| Code | Meaning | Likely cause | First action |
| --- | --- | --- | --- |
| G11 | Fail to start | Weak starter battery (PG-BAT-12), fuel starvation | Check battery voltage (≥ 12.4 V at rest); replace PG-BAT-12 if below |
| G14 | Low fuel pressure | Clogged fuel filter (PG-FLT-F), air in fuel line | Replace fuel filter kit and bleed the line |
| G21 | Output voltage unstable | Failed automatic voltage regulator (PG-AVR-3) | Measure output; replace PG-AVR-3 if voltage swings more than ±5% |
| G30 | High coolant temperature | Low coolant, blocked radiator | Let it cool fully before opening; top up and inspect radiator |
| G40 | Emergency stop activated | E-stop button pressed | Find out why it was pressed before resetting |

# 3. Weekly test

Customers should run the generator off-load for 15 minutes every week. Missed weekly tests are the most common cause of G11 failures.

# 4. Standard repair times

| Job | Time |
| --- | --- |
| Replace starter battery | 30 min |
| Replace fuel filter kit | 1 hour |
| Replace AVR | 2 hours |

# 5. Safety

Never open the radiator cap on a hot engine.

Diesel smell or fuel on the floor: stop the generator, ventilate and treat as a fuel leak.

Ensure the generator is in OFF / manual mode before working, so it cannot auto-start.